## KS Group (2)
WORKING SCHEDULE
Name of Work:- Upgradation of Distribution Transformer from 100 KVA to 200 KVA due to increase of load at K.S. Group of Industries, Unit-1 plant, Harinakhala within the jurisdiction of Mohanpur Electrical Sub Division.(Partial Trunkey Basis).
Ch to:- Deposit work with Dibyendu Choudhury, K.S. Group of Industries, Unit-1, Vill- Harinakhala, P.O- Fatikcherra, (Near SDM Office), Sidhai Mohanpur, Tripura West.
SL. No. | Description of items | Supply |  |  |  | Erection |  |  |  | Total Amount (A+B=X)
|  | Unit | Qnty | Rate | Amount (A) | Unit | Qnty | Rate | Amount (B)
A | Carriage of Materials
1 | Carriage of 9.0 mtr long length of PCC Pole by mechanical transport from Sub-Divisional stack yard to working site vis-à-vis including loading, unloading and stacking as required (Upto 4 Pole) | No. |  |  |  | No. | 1
2 | Carrying of Store materials from MM Store,AD Nagar to Electrical Sub-Divisional Store-yard to by Mechanical Transport/hand cart, manual labour including loading, unloading,stacking etc. as required. (Beyond 25 KM up to lead of 50KM) | No |  |  |  | No | 3
3 | Carriage of 11/0.430, 3-Phase 200 KVA Transformer by mechanical transport from the store to working site vis-à-vis including loading, unloading, placing on base as required | No. |  |  |  | No. | 1
4 | Carriage of 11/0.430, 3-Phase 100 KVA Transformer by mechanical transport from working site to ESD- Store vis-à-vis including loading, unloading, placing on base as required | No. |  |  |  | No. | 1
5 | Hiring of vehicle for site visit/work inspection | No. |  |  |  | No. | 3
B | Dismantling of Following
1 | Dismantling of 11/0.430 KV, 3-Phase 100 KVA Distribution Transformer on Pole with necessary connections. | No. |  |  |  | No. | 1
2 | Dismantling three phase service connection with PVC cable from nearby Electrical Pole to premises i/c G.I.Wire, Reel Insulator | No. |  |  |  | No. | 1
C | Supply and erection of Following
1 | Erection of the following PCC pole direct in earth including excavation,back filling & ramming etc. as required (the poles should be buried 1/6th of their length ) as per technical specification as per direction of the Engineering In Charge.
| a) 9.0 Mtr. Long PCC Pole | No. | TSECL SUPPLY |  |  | No. | 2
2 | Erection of Stay set complete direct in earth with 19mmX1800mm long stay rod,anchor plate of size of 300x300x8mm,turn buckle,7/2.5mm.G.I stranded stay wire and 11KV / LT guy insulator etc as direction of Engg.In-Charge. | Set | TSECL SUPPLY |  |  | Set | 2
3 | Erection including commissioning of 11/0.440KV,200 KVA three phase Distribution Transformer support with all necessary accessories and fittings as per T.S. etc. as reqd. as per direction of the Engineering In Charge. (Warrenty period should covered two years from the date of installation) | No. | TSECL SUPPLY |  |  | No. | 1
4 | Stringing of ACSR (6/1/2.59mm dia.weasel) including laying, hoisting, binding & Jumpering etc.as required as per technical specification etc. as reqd.as per direction of the Engineering In Charge. | KM | TSECL SUPPLY |  |  | KM | 0.2
5 | Supply and erection of fabricated Cross arm 1.3 to 2.8 mtr. Long M.S channel 75X40X40X6mm (excluding the cost of bracket clamp, nuts & bolts. | Kg | TSECL SUPPLY |  |  | No. | 3
6 | Supply and erection of fabricated Cross arm 0.3 to 1.2 mtr. Long M.S channel 75X40X40X6mm (excluding the cost of bracket clamp, nuts & bolts. | Kg | TSECL SUPPLY |  |  | No. | 2
7 | Providing Three Phase Service connection with laying PVC cable from nearby Electrical Pole to premises upto 35 mtr in length supported by G.I.Wire, Reel Insulator i/c fitting fixing of Energy Meter as required. | No | TSECL SUPPLY |  |  | No. | 1
8 | Fitting & fixing of LT Cut Out (set of 3 Nos) on wooden plank of size 24"x10"x15" & cable connection with termination by thimbles(inc supply of wooden plank, screw & MS clamp excluding cost of thimble). | Set | TSECL SUPPLY |  |  | Set | 1
9 | Earthing with 2.5 mtr long G.I. Pipe (ISI Marked) of 40 mm dia with holes including a pair of clamps of 50x6 mm MS flat & 12 mm dia galvanized nuts & bolts along with alternate layer of salt and charcoal with supply of G.I. Pipe as per REC Specification and design | Nos. | 0 | 0 | 0 | Nos. | 2
10 | Laying of 8 SWG GI wire at 300 mm below the ground level for earthing of sub-station equipment from the earth electrode. | Nos. | TSECL SUPPLY |  |  | Nos. | 2
D | Supply of the Following
1 | Supply transortation unloading deilvery at worksite installation and commisiomn of outdoor cubical type pole/wall mounted 11KV 3 phase metering panel made of stell sheet (thickness of 2mm) duly painted and powder coated with CT PT combined unit of CT ratio 100/5 A & PT ratio 11000/110 volt digital KWH meter ammeter and volmeter LED indication lamps and provision for necessary connection of cable etc as per requirment (Warrenty period should covered two years from the date of installation) | No. | 1 |  |  | No. | 0
2 | Supply of Bracket Clamp of size (50x6mm) MS flat. etc. as reqd. | No. | 10 |  |  | No. | 0
3 | Supply of Stay Clamp of size (50x6mm) MS flat. etc. as reqd. | Pair | 2 |  |  | Pair | 0
4 | Supply of 60kg, Salt & 55kg Charcoal(For 1 Pit) | Nos. | 2 |  |  | Nos. | 0
5 | Supply of 2.5mtr, Long, 40mm dia G.l. pipe Make. TATA/JINDAL) | Nos. | 2 |  |  | Nos. | 0
E | Civil Work
1 | Supply and Providing of sub-station protective fencing of size 2X3Mtr.and height 1.5Mtr. as per Engineering requirement by 10nos MS angle post( 50x50x6mm) of height of 2(two) metre horizontal bar 2x3mtr and 2x2mtr MS Angle( 35x35x5mm) at top of angle posts and two part MS grill door of size 1.2/1.4 with locking arrangement in/c necessary grouting and painted by Al paint over red oxide priming of approval quality as requirement as per TS in/c supply of all materials as per direction of the Engineering In-Charge. | Nos. | 0 |  |  | Nos. | 1
2 | Fabrication of MS Angle/Channel | Nos. | 0 |  |  | Kg | 86
TOTAL