## BOQ Laddu chowmohani
WORKING ESTIMATE
Name of work : - Extension of HT line and construction of 1x100 KVA substation for providing service connection to Modified IRP including DTW at Laddhu chowmohani near the H/O Nikhil ch shil Ward no-08 under Bodhjungnagar Electrical Sub-Division.
DNIT No. DGM/ED-RNB/2024-25/ 03 Dated- 06 /01/2025
Chargeable to :- DEPOSIT WORK WITH Assistant engineer DWS Division no-III, Kunjaban , Agartala.
Sl.NO. | Description of work | Supply & Errection
|  | Qty. | Unit | Rate | Amount
1 | Carrying of 9 mtr long PCC pole from PCC pole manufacturing Unit Ambassa to Subdivisional store By Mechanical Transport / Handcart / Mannual labour Etc as required including Loading / Unloading & stacking as per Direction of Eng in Charge.
a | Beyond25 km upto the lead of 50 km
i | for maximum 4( four) poles | 1 | trip
b | Beyond 50 km additional amount of every 25 km. | 2 | Nos
2 | Carrying of 9 mtr long PCC pole from PCC pole from Subdivisional store yard to work site site By Mechanical Transport / Handcart / Mannual labour Etc as required including Loading / Unloading & stacking as per Direction of Eng in Charge.
a | Beyond25 km upto the lead of 50 km
i | for maximum 4( four) poles | 1 | trip
ii | Beyond 4(four) poles | 0 | Nos
3 | Carriage of Materials such as Cable, AAS, AAAC, ACSR,GI wire, Cross arm, Stay set, insulator etc by Mechanical Transport from the Electrical Sub-Divisional site Store to working site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 2
4 | Carrying of GOS, DOF, LA etc by Mechanical Transport from the Electrical Sub-Divisional site Store to working site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 2
5 | Carrying of 100 KVA Transformer etc by Mechanical Transport from the central store subdivision to Sub-Divisional site Store vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 1
6 | Carrying of 100 KVA Transformer etc by Mechanical Transport from the Sub Divisional store to Work site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 1
7 | Detailed survey of line | 0.25 | km
8 | Erection of following Poles direct in Earth in/c Excavation , Back filling & ramming etc as Required ( the poles should be Burried 1/6 th of it's length) as per Technical Specification.
a | 9.0Mtr long PCC Pole | 2 | Nos.
9 | Erection of painted stay set complete direct in earth with 16 mm dia 1.8 mtr long painted stay rod anchor plate of size 300x300x8 mm thick, turn buckle of length 356 mm with 300mm long threaded adjustable 16 mm dia MS rod and thimble inc erection of 11 KV/LT guy insulator , galvanised stay stranded wire etc as per direction of Eng -in - charge. | 5 | set
10 | Installation of 100 KVA Transformer | 1 | Nos.
11 | Erection of fabricated MS channel / Angle cross arms with clamps , N/B Complete as reqd on poles as per T.S
i | 1.2 mtr. Long MS Ch (75X40X40X6)mm for SP bottom cross arm | 2 | Nos.
ii | 2.8 mtr. Long MS Ch (75X40X40X6mm) for GOS base support. | 12 | Nos.
iii | 0.8 mtr. Long MS Ch (75X40X40X6mm) for GOS base support. | 4 | Nos.
iv | 1.5 mtr long S P pole guard bkt ( 65x65x6mm) | 2 | Nos.
v | 2.5 mtr long double pole guard bkt ( 65x65x6mm) | 1 | Nos.
12 | Fabrication of Channel/ Angle / MS flate as per specification. | 410.24 | kg
13 | Erection of 11 KV polymaric Pin insulator. | 12 | Nos.
14 | Erection & connection of triple pole ( 3 ph , 12 KV , 200 A manually Gang operated air Brek switch including necessary Connection | 2 | set
15 | Erection & connection of triple pole ( 3 ph , 12 KV , 200 A manually DOF Connection | 1 | set
16 | 11 KV Poly Maric LA | 3 | Nos.
17 | Supply of 3 phase, 3 core, 70 sqmm,6.35/11KV, XLPE insulated aluminium power cable . | 0.2 | km
18 | Laying & comissioning of 3 phase, 3 core, 70 sqmm,6.35/11KV, XLPE insulated aluminium power cable direct in earthi/c excavation of earth upto a trench depth of 1100mm & a width of 500mm inc supply & protection by two layer 1st class brick soiling, 150 mm layer of sand soiling, crushing , refeling & ramming or asper site requirement as per direction of Eng-in- charge. ( 1 no spare) | 0.2 | km
19 | HDPE pipe PE-100 Grade 110 mm outer Dia. | 15 | mte
20 | HDPE pipe PE-100 Grade 110 mm outer Dia. | 15 | mte
21 | Supply and Making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core , XLPE aluminium conductor cable of 11 KV grade as required .( upto 150 sq mm) | 3 | Nos.
22 | Supply and Making Out door cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core , XLPE aluminium conductor cable of 11 KV grade as required .( upto 150 sq mm) | 3 | Nos.
23 | Stringing of G.I Wire 8 SWG GI wire inc laying , hoisting, binding etc as required as per TS | 0.1 | km
24 | Breaket Clamp Made by 50x6mm | 32 | Nos.
25 | Stay Clamps made by 50x6mm | 1 | Nos.
26 | Erection of pipe earthing with supply of salt and charcoal clamps N/B inc Excavation , refilling with alternate layer of salt and charcoal and providing connection of earthing materials and equipment to earth electrode as per REC specification & design. | 3 | Nos.
27 | Supply of 2.5mt long 40mm dia GI Pipe (Make TATA / JINDAL) | 3 | Nos.
28 | Supply of 60 Kg Salt & 55Kg Charcoal for 1Pit. | 3 | Nos.
29 | Laying of 8SWG GI wire at 300mm below the ground level for earthing of Sub-Station equipments from the earth electrod. | 3 | Nos.
Total
DEPUTY GENERAL MANAGER
ELECTRICAL DIVISION-RANIRBAZAR
RANIRBAZAR TRIPURA WEST
WEST TRIPURA
Manager (Electrical)
Bodhjungnagar Elect. Sub-Division
West Tripursa

## BOQ Bardhan Para
Working Estimate
Name of work : - Estimate for extension of HT line and construction of 1x100 KVA substation for providing service connection to Modified IRP including DTW at Bardhan para ( Paul para ) Ward No-8 under Bodhjungnagar Electrical Sub-Division.
DNIT No. DGM/ED-RNB/2024-25/ 02 Dated- 20 /12/2024
Chargeable to :- DEPOSIT WORK WITH Assistant engineer DWS Division no-III, Kunjaban , Agartala.
Sl.NO. | Description of work | Supply & Errection
|  | Qty. | Unit | Rate | Amount
1 | Carrying of 9 mtr long PCC pole from PCC pole manufacturing Unit Ambassa to Subdivisional store By Mechanical Transport / Handcart / Mannual labour Etc as required including Loading / Unloading & stacking as per Direction of Eng in Charge.
a | Beyond25 km upto the lead of 50 km
i | for maximum 4( four) poles | 1 | trip
b | Beyond 50 km additional amount of every 25 km. | 2 | nos
2 | Carrying of 9 mtr long PCC pole from PCC pole from Subdivisional store yard to work site site By Mechanical Transport / Handcart / Mannual labour Etc as required including Loading / Unloading & stacking as per Direction of Eng in Charge.
a | Beyond25 km upto the lead of 50 km
i | for maximum 4( four) poles | 1 | trip
ii | Beyond 4(four) poles | 0 | nos
3 | Carriage of Materials such as Cable, AAS, AAAC, ACSR,GI wire, Cross arm, Stay set, insulator etc by Mechanical Transport from the Electrical Sub-Divisional site Store to working site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 2
4 | Carrying of GOS, DOF, LA etc by Mechanical Transport from the Electrical Sub-Divisional site Store to working site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 2
5 | Carrying of 100 KVA Transformer etc by Mechanical Transport from the central store subdivision to Sub-Divisional site Store vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 1
6 | Carrying of 100 KVA Transformer etc by Mechanical Transport from the Sub Divisional store to Work site vis-à-vis in/c loading unloading and stacking as required upto the lead of 25 KM. | 1
7 | Detailed survey of line | 0.25 | Km
8 | Erection of following Poles direct in Earth in/c Excavation , Back filling & ramming etc as Required ( the poles should be Burried 1/6 th of it's length) as per Technical Specification.
i | 9.0Mtr long PCC Pole | 2 | Nos.
9 | Erection of painted stay set complete direct in earth with 16 mm dia 1.8 mtr long painted stay rod anchor plate of size 300x300x8 mm thick, turn buckle of length 356 mm with 300mm long threaded adjustable 16 mm dia MS rod and thimble inc erection of 11 KV/LT guy insulator , galvanised stay stranded wire etc as per direction of Eng -in - charge. | 5 | Set
10 | Installation of 100 KVA Transformer | 1 | Nos.
11 | Erection of fabricated MS channel / Angle cross arms with clamps , N/B Complete as reqd on poles as per T.S
i | 1.2 mtr. Long MS Ch (75X40X40X6)mm for SP bottom cross arm | 2 | Nos.
ii | 2.8 mtr. Long MS Ch (75X40X40X6mm) for GOS base support. | 12 | Nos.
iii | 0.8 mtr. Long MS Ch (75X40X40X6mm) for GOS base support. | 4 | Nos.
iv | 1.5 mtr long S P pole guard bkt ( 65x65x6mm) | 2 | Nos.
v | 2.5 mtr long double pole guard bkt ( 65x65x6mm) | 1 | Nos.
12 | Fabrication of Channel/ Angle / MS flate as per specification. | 410.24 | kg
13 | Erection of 11 KV polymaric Pin insulator. | 12 | Nos.
14 | Erection & connection of triple pole ( 3 ph , 12 KV , 200 A manually Gang operated air Brek switch including necessary Connection | 2 | Set
15 | Erection & connection of triple pole ( 3 ph , 12 KV , 200 A manually DOF Connection | 1 | Set
16 | 11 KV Poly Maric LA | 3 | Nos.
17 | Supply of 3 phase, 3 core, 70 sqmm,6.35/11KV, XLPE insulated aluminium power cable . | 0.5 | km
18 | Laying & comissioning of 3 phase, 3 core, 70 sqmm,6.35/11KV, XLPE insulated aluminium power cable direct in earthi/c excavation of earth upto a trench depth of 1100mm & a width of 500mm inc supply & protection by two layer 1st class brick soiling, 150 mm layer of sand soiling, crushing , refeling & ramming or asper site requirement as per direction of Eng-in- charge. ( 1 no spare) | 0.5 | km
19 | HDPE pipe PE-100 Grade 110 mm outer Dia. | 15 | mte
20 | HDPE pipe PE-100 Grade 110 mm outer Dia. | 15 | mte
21 | Supply and Making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core , XLPE aluminium conductor cable of 11 KV grade as required .( upto 150 sq mm) | 3 | Nos
22 | Supply and Making Out door cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core , XLPE aluminium conductor cable of 11 KV grade as required .( upto 150 sq mm) | 3 | Nos
23 | Stringing of G.I Wire 8 SWG GI wire inc laying , hoisting, binding etc as required as per TS | 0.1 | Km
24 | Supply of Breaket Clamp Made by 50x6mm | 32 | Nos.
25 | Supply of Stay Clamps made by 50x6mm | 1 | Nos.
26 | Erection of pipe earthing with supply of salt and charcoal clamps N/B inc Excavation , refilling with alternate layer of salt and charcoal and providing connection of earthing materials and equipment to earth electrode as per REC specification & design. | 3 | Nos.
27 | Supply of 2.5mt long 40mm dia GI Pipe (Make TATA / JINDAL) | 3 | Nos.
28 | Supply of 60 Kg Salt & 55Kg Charcoal for 1Pit. | 3 | Nos.
29 | Laying of 8SWG GI wire at 300mm below the ground level for earthing of Sub-Station equipments from the earth electrod. | 3 | Nos.
Total
DEPUTY GENERAL MANAGER
ELECTRICAL DIVISION-RANIRBAZAR